## How To
Duplicate tabs below as needed.
Use 'Two 1-D Components' for most details - when only two unique components make up the thermal bridge calculation.
Use 'Three 1-D Components' when three unique components make up the thermal bridge calculation.
Enter project information.
Move red box to select general location of bridge calculated.
Enter appropriate values from THERM calculation.
Screenshot appropriate images as described in boxes.
Select Cells A1-U70
File > Print > PDF > Print Selection Only > Fit all Columns on Page for single page report.
V2.4
2022-04-18

## Two 1-D Components
Phius Thermal Bridging Psi-Value Calculator & Report v2.4
Detail view
Detail
Description
File name
Project name
Project #
Date
Company
General Scheme (select)
[6 empty] | Boundary |  |  | Surface
[6 empty] | Conditions |  | T (F) | Film
Resist.
[6 empty] | Indoor |  |  | (R-Value)
[6 empty] | Wall | Ex. | 68 | 0.74 | Material View
[6 empty] | Roof | Ex. | 68 | 0.57
[6 empty] | Floor | Ex. | 68 | 0.97
Outdoor
[6 empty] | Ambient | Ex. | 14 | 0.23/0.45
[6 empty] | Ground | Ex. | 41 | 0
*Enter values from THERM into yellow cells
|  |  |  | U | dT | L | ULdT | error
| 2D model |  |  | (btu/hr.sf.F) | (F) | (in) | (btu/hr.ft) | (%)
|  |  | Interior |  |  |  | 0
|  |  | Exterior |  |  |  | 0
Isotherm view
| Component |  |  | U | dT | L | ULdT | error
|  |  |  | (btu/hr.sf.F) | (F) | (in) | (btu/hr.ft) | (%)
| Component A |  | Interior |  |  |  | 0
|  |  | Exterior | 0 | 0 | 0 | 0 | 0%
| Component B |  | Interior |  |  |  | 0 |  |  |  | `
|  |  | Exterior | 0 | 0 | 0 | 0 | 0%
| Psi |  |  | PsidT | dT | Psi | Psi for WUFI
| #DIV/0! |  |  | (btu/hr.ft) | (F) | (btu/hr.ft.F) | (btu/hr.ft.F)
|  |  | Interior | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | Exterior | 0 | 0 | #DIV/0!
#DIV/0!
Component A |  |  |  |  | Component B |  |  |  |  | Infrared
Note on C19: Drag-and-drop red outline to show general location of thermal bridge detail.

## Three 1-D Components
Phius Thermal Bridging Psi-Value Calculator & Report v2.4
Detail view
Detail
Description
File name
Project name
Project #
Date
Company
General Scheme (select)
[6 empty] | Boundary |  |  | Surface
[6 empty] | Conditions |  | T (F) | Film
Resist.
[6 empty] | Indoor |  |  | (R-Value)
[6 empty] | Wall | Ex. | 68 | 0.74 | Material View
[6 empty] | Roof | Ex. | 68 | 0.57
[6 empty] | Floor | Ex. | 68 | 0.97
Outdoor
[6 empty] | Ambient | Ex. | 14 | 0.23/0.45
[6 empty] | Ground | Ex. | 41 | 0
*Enter values from THERM into yellow cells
|  |  |  | U | dT | L | ULdT | error
| 2D model |  |  | (btu/hr.sf.F) | (F) | (in) | (btu/hr.ft) | (%)
|  |  | INT | 0.0209 | 54 | 132.965 | 12.5054 | 1.68%
|  |  | EXT | 0.0153 | 54 | 181.455 | 12.4932 | 1.68%
Isotherm view
| Component |  |  | U | dT | L | ULdT | error
|  |  |  | (btu/hr.sf.F) | (F) | (in) | (btu/hr.ft) | (%)
| Component A |  | INT |  |  |  | 0
|  |  | EXT | 0 | 0 | 0 | 0 | 0%
| Component B |  | INT |  |  |  | 0
|  |  | EXT | 0 | 0 | 0 | 0 | 0%
| Component C |  | INT |  |  |  | 0
|  |  | EXT | 0 | 0 | 0 | 0 | 0%
| Psi |  |  | PsidT | dT | Psi | Psi for WUFI
|  |  |  | (btu/hr.ft) | (F) | (btu/hr.ft.F) | (btu/hr.ft.F)
|  |  | INT | 12.5054 | 54 | 0.23158 | 0.23147
|  |  | EXT | 12.4932 | 54 | 0.23136
Component A |  |  | Component B |  |  |  | Component C |  |  | Infrared
Note on C19: Drag-and-drop red outline to show general location of thermal bridge detail.

## Example
Phius Thermal Bridging Psi-Value Calculator & Report v2.4
Detail view
Detail
| Description |  | Typical Perimeter
| File name |  | Example File
| Project name |  | n/a
| Project # |  | n/a
| Date |  | 2018-12-10
| Company |  | PHIUS
General Scheme (select)
[7 empty] | Boundary |  |  | Surface
[7 empty] | Conditions |  | T (F) | Film
Resist.
[7 empty] | Indoor |  |  | (R-Value)
[7 empty] | Wall | Ex. | 68 | 0.74 | Material View
[7 empty] | Roof | Ex. | 68 | 0.57
[7 empty] | Floor | Ex. | 68 | 0.97
Outdoor
[7 empty] | Ambient | Ex. | 14 | 0.23/0.45
[7 empty] | Ground | Ex. | 41 | 0
*Enter values from THERM into yellow cells
| 2D model |  |  |  | U | dT | L | ULdT | error
[5 empty] | (btu/hr.sf.F) | (F) | (in) | (btu/hr.ft) | (%)
|  |  |  | INT | 0.01 | 54 | 97.9955 | 4.4098 | 1.74%
|  |  |  | EXT | 0.002 | 54 | 497.193 | 4.4747 | 1.74%
Isotherm view
| Component |  |  |  | U | dT | L | ULdT | error
[5 empty] | (btu/hr.sf.F) | (F) | (in) | (btu/hr.ft) | (%)
| Component A |  |  | INT | 0.0227 | 54 | 55 | 5.6182 | 0%
| Wall |  |  | EXT | 0.0227 | 54 | 55 | 5.6182 | 0%
| Component B |  |  | INT | 0.0614 | 27 | 60.25 | 8.3235 | 0%
| Slab |  |  | EXT | 0.0614 | 27 | 60.25 | 8.3235 | 0%
| Psi |  |  |  | PsidT | dT | Psi | Psi for WUFI
[5 empty] | (btu/hr.ft) | (F) | (btu/hr.ft.F) | (btu/hr.ft.F)
|  |  |  | INT | -9.532 | 54 | -0.17652 | -0.17592
|  |  |  | EXT | -9.4671 | 54 | -0.17532
PHIUS recommends against taking negative thermal bridges in the design phase. See Thermal Bridges section in Certification Guidebook.
Component A | [5 empty] | Component B |  |  |  |  | Infrared
Note on C19: Drag-and-drop red outline to show general location of thermal bridge detail.

## Example 2
Phius Thermal Bridging Psi-Value Calculator & Report v2.4
Detail view
Detail
| Description |  | Emery Street Foundation Perimeter
| File name |  | PHIUS CPHC Training THERM Tutorial
| Project name |  | Emery Street
| Project # |  | 1243
| Date |  | 2019-03-27
| Company |  | PHIUS CPHC Training
General Scheme (select)
[7 empty] | Boundary |  |  | Surface
[7 empty] | Conditions |  | T (F) | Film
Resist.
[7 empty] | Indoor |  |  | (R-Value)
[7 empty] | Wall | Ex. | 68 | 0.74 | Material View
[7 empty] | Roof | Ex. | 68 | 0.57
[7 empty] | Floor | Ex. | 68 | 0.97
Outdoor
[7 empty] | Ambient | Ex. | 14 | 0.23/0.45
[7 empty] | Ground | Ex. | 41 | 0
*Enter values from THERM into yellow cells
[5 empty] | U | dT | L | ULdT | error
| 2D model |  |  |  | (btu/hr.sf.F) | (F) | (in) | (btu/hr.ft) | (%)
|  |  |  | Interior | 0.0426 | 27 | 84.0368 | 8.0549 | 7.7%
|  |  |  | Exterior | 0.0249 | 27 | 144.148 | 8.0759 | 7.7%
Isotherm view
| Component |  |  |  | U | dT | L | ULdT | error
[5 empty] | (btu/hr.sf.F) | (F) | (in) | (btu/hr.ft) | (%)
| Component A |  |  | Interior | 0.0315 | 27 | 55.054 | 3.902 | 0%
| Wall 1D |  |  | Exterior | 0.0315 | 27 | 55.054 | 3.902 | 0%
| Component B |  |  | Interior | 0.0396 | 27 | 55.012 | 4.9016 | 0% |  |  | `
| Slab 1D |  |  | Exterior | 0.0396 | 27 | 55.012 | 4.9016 | 0%
| Psi |  |  |  | PsidT | dT | Psi | Psi for WUFI
[5 empty] | (btu/hr.ft) | (F) | (btu/hr.ft.F) | (btu/hr.ft.F)
|  |  |  | Interior | -0.74859 | 27 | -0.027726 | -0.027337
|  |  |  | Exterior | -0.72763 | 27 | -0.026949
PHIUS recommends against taking negative thermal bridges in the design phase. See Thermal Bridges section in Certification Guidebook.
Component A | [5 empty] | Component B |  |  |  |  | Infrared
Note on C19: Drag-and-drop red outline to show general location of thermal bridge detail.